## Summary
|  | Paithan |  | Guwahati |  | Chitegaon |  | Pithampur |  | Dahej |  |  |  |  | 9227866.6667
S.No. | Spare Part Description | QTY | Frequency | Qty | Frequency | Qty | Frequency | Qty | Frequency | Qty | Frequency | To be Frequency | No. of Filters to be saved each year | To be implemented | Cost benefit considering INR 7000 as average cost of filter
1 | Compressed air line filters 0.2 micron rating (5 inches & 10 inches) | 100 | 1 | 150 | 1 | 13 | 1 | 29 | 1 | 170 | 1 | 2 years | 231 | Yes | 1617000
2 | Vaccum cleaner filter details -HEPA filter H=122 (SO2881) | 75 | 1 | 60 | 1 |  |  | 19 | 1 | 67 | 1 | 2 years | 110.5 | No | 773500
3 | Dust collector filter (300,600,900,1200 CFM) | 40 | 5 | 20 | 5 | 3 | 5 | 12 | 5 | 60 | 5 | 6 years | 22.5 | No | 157500
4 | HVAC - Process Cleaning Area - HEPA filter | 90 | 4 | 602 | 4 | 26 | 6 | 310 | 6 | 384 | 4 | 5 years | 215.2 | No | 1506400
5 | HVAC - Process Cleaning Area - Geal Seal |  |  | 308 | 4 | [6 empty] | 5 years | 61.6 | No | 431200
6 | HVAC - Process Cleaning Area -Super HEPA | 35 | 4 | 100 | 4 | 10 | 6 |  |  |  |  | 5 years | 55 | No | 385000
7 | HVAC - Process Cleaning Area -F-9 | 8 | 4 | 10 | 4 | [6 empty] | 5 years | 3.6 | No | 25200
8 | HVAC of Non Process area - HEPA filter replacement (0.3 Micron) | 60 | 5 | 172 | 5 | 14 | 5 | 170 | 6 | 618 | 5 | 6 years | 28.8 | Yes | 201600
9 | HVAC of Process area -HVAC Filter replacement (3 Micron and 10 Micron) | 200 | 5 | 1708 | 5 | 55 | 5 | 440 | 5 | 458 | 5 | 6 years | 476.8333 | No | 3337833.3333
10 | HVAC of Non Process area - HVAC Filter replacement (3 Micron,10 Micron and 20 Micron) | 225 | 5 | 1832 | 5 | 70 | 5 | 675 | 5 | 595 | 5 | 6 years | 113.2333 | Yes | 792633.3333
11 | HVAC of Process area-HVAC Return Filter replacement (20 Micron) | 100 | 3 | 267 | 3 | 15 | 5 | 100 | 5 | 326 | 3 | 5 years | 96.4 | No | 674800
12 | Nitrogen generator filter housing replacement | 10 | 2 |  |  | 2 | 2 | 4 | 2 | 7 | 2 | No Change |  |  | 0
13 | Purified water tank vent filter replacement | 1 | 10 months | 15 | 6 months | 2 | 10 months | 5 | 12 months | 3 | 6 months | No Change |  |  | 0
14 | HEPA filter 250mm dia x 90mm long for Dust collector filter; 0.492 m2 area; 180CFM Dust Collector Make:- Kambert, Type:- KDM-180. |  |  | 250 | 5 | 2 | 5 |  |  |  |  | No Change |  |  | 0

## Filter Data
Date : Mar 06, 2024
Subject: | Filters replacement frequency
Sr. No. | Filter Details | Filter replacement details
Site Name
|  | Paithan |  |  | Guwahati |  |  | Chitegaon |  |  | Pitampur |  |  | Dahej
|  | Filter type | Qty. Require | Frequency | Filter type | Qty. Require | Frequency | Filter type | Qty. Require | Frequency | Filter type | Qty. Require | Frequency | Filter type | Qty. Require | Frequency
1 | Compressed air line filters 0.2 micron rating (5 inches & 10 inches) | 0.2 micron | 100 | Once in year | 0.2 micron | 150 | Once in year | 0.2 Micron, 5 Inch Long | 13 | Once in Year and as an when required. | 0.2 micron | 29 | Once in year | 0.2 micron | 167 | Once in year
2 | Vaccum cleaner filter details -HEPA filter H=122 (SO2881) | H=122 | 75 | Once in year & As and when require | H=122 | 60 | Once in year & As and when require | NA |  |  | H=122 | 19 | Once in year & As and when require | H=122 | 67 | Once in year & As and when require
3 | Dust collector filter (300,600,900,1200 CFM) | Dust collector filter | 40 | Once in 5 Year | Dust collector filter | 20 | Once in 5 Year | Dust collector filter | 3 | Once in 5 Year and when required. | Dust collector filter | 12 (Once in Five year) | Once in 5 Year and As and when require | Dust collector filter | 60 | Once in 5 Year
4 | HVAC of Process area -HEPA filter/Super HEPA/F-9 HEPA filter replacement (0.3 Micron) | HEPA filter | 90 | 4 year or as and when required. | HEPA filter | 602 | 4 year or as and when required | HEPA filter | 26 | 4 year or as and when required. | HEPA filter | 310 (Once in Six year) | 6 year or as and when required. | HEPA filter | 384 | 4 year or as and when required.
|  | Geal Seal | NA |  | Geal Seal | 308 |  | Geal Seal | NA |  | Geal Seal | NA |  | Geal Seal
|  | Super HEPA | 35 |  | Super HEPA | 100 |  | Super HEPA | 10 |  | Super HEPA | NA |  | Super HEPA | NA
|  | F-9 | 8 |  | F-9 | 10 |  | F-9 | NA |  | F-9 | 2 (Once in Six year) |  | F-9 | NA
5 | HVAC of Non Process area - HEPA filter replacement (0.3 Micron) | HEPA filter | 60 | 5 year or as and when required. | HEPA filter | 172 | 5 year or as and when required. | HEPA filter | 14 | 5 year or as and when required. | HEPA filter | 170 (Once in Six year) | 6 year or as and when required. | HEPA filter | 618 | 5 year or as and when required.
6 | HVAC of Process area -HVAC Filter replacement (3 Micron and 10 Micron) | 3 Micron | 100 | 5 year or as and when required. | 3 Micron | 875 | 5 year or as and when required. | 3 Micron | 25 | 5 year or as and when required. | 3 Micron | 220 (Once in Five year) | 5 year or as and when required. | 3 Micron | 224 | 5 year or as and when required.
|  | 10 Micron | 100 |  | 10 Micron | 833 |  | 10 Micron | 30 | NA | 10 Micron | 220 (Once in Five year) |  | 10 Micron | 234
7 | HVAC of Non Process area - HVAC Filter replacement (3 Micron,10 Micron and 20 Micron) | 3 Micron | 100 | 5 year or as and when required. | 3 Micron | 875 | 5 year or as and when required. | 3 Micron | 25 | 5 year or as and when required. | 3 Micron | 255 (Once in Five year) | 5 year or as and when required. | 3 Micron | 595 | 5 year or as and when required.
|  | 10 Micron | 100 |  | 10 Micron | 833 |  | 10 Micron | 30 |  | 10 Micron | 250 (Once in Five year) |  | 10 Micron | 583
|  | 20 Micron | 25 |  | 20 Micron | 124 |  | 20 Micron | 15 |  | 20 Micron | 170 (Once in Five year) |  | 20 Micron | NA
8 | HVAC of Process area-HVAC Return Filter replacement (20 Micron) | 20 Micron | 100 | 3 year or as and when required. | 20 Micron | 267 | 3 year or as and when required. | 20 Micron | 15 | 5 year or as and when required. | 20 Micron | 100 | 5 year or as and when required. | 20 Micron | 326 | 3 year or as and when required.
9 | Nitrogen generator filetr housing replacement | NA | 10 | 2 year or as and when required. | NA | NA | NA | NA | 2 | 2 year or as and when required. | NA | 4 | 2 year or as and when required. | NA | 7 | 2 year or as and when required.
10 | Purified water tank vent filter replacement | 0.2 Micron | 1 | 10 Months | 0.2 Micron | 15 | 6 Months | 0.2 Micron | 2 | 10 Month or as and when required. | 0.2 Micron | 5 | 12 Months (-30 Days) | 0.2 Micron | 3 | 6 Months
11 | HEPA filter 250mm dia x 90mm long for Dust collector filter; 0.492 m2 area; 180CFM Dust Collector Make:- Kambert, Type:- KDM-180. | NA | NA | NA | 5 Micron | 250 | 5 year or as and when required. | 0.3 Micron HEPA | 2 | 5 year or as and when required. | NA | NA | NA | NA | NA | NA
12 | Bag filter for dust collector filter material :- Food grade micron filter; 180CFM Filteration Dust Collector Make:- Kambert, Type:- KDM-180. | NA | NA | NA | NA | NA | NA | 0.3 Micron Bag filter | 2 |  | NA | NA | NA | NA | NA | NA